Exit Signs – Code Compliant Photoluminescent Exit Signs for Use Above the Door and at Floor Level

PART 1 GENERAL

1.1	SECTION INCLUDES

- Above the door (high level) exit signs tested and evaluated to the UL924 performance standard.

- Floor level (low level) exit signs tested and evaluated to the UL924 performance standard.

- Wall mounted without a mounting bracket.

- Wall or ceiling mounted with a mounting bracket.

- Single side and double side exit signs tested and evaluated to the UL924 performance standard.

1.2	DESCRIPTION

This project will use aluminum (NOT plastic, vinyl or PVC) photoluminescent type exit signs and frames in both high and low locations to the greatest possible extent.  The use of aluminum signs provides the building owner code compliant sustainable exit signs with minimum environmental impact and 100% recyclable construction.  Qualified aluminum exit sign faces, frames and mounting brackets must be virtually 100% aluminum (the ink, glow pigment and fasteners are not aluminum) and constructed of a minimum of 60% post consumer recycled aluminum.  Plastic exit signs (signs containing vinyl or PVC emit dioxins and other toxic materials when incinerated) can have adverse environmental consequences and should be avoided.  Radioluminescent exit signs should be avoided because they contain radioactive tritium gas (a hazard which must be registered with the Nuclear Regulatory Commission) and can cause radiation contamination resulting in danger to life or costly site clean-up if the signs are damaged or if they are not disposed of properly.  In those areas where photoluminescent exit signs can not be used, LED type exit signs with minimal environmental impact will be used.

Photoluminescent (PL) exit signs are included in this Section because they are charged from nearby fluorescent lighting fixtures and therefore the facility lighting near these signs must be designed, installed and tested to properly illuminate the PL exit signs.

This Section specifies the engineering, procurement, installation and testing of photoluminescent exit signs for high and low level applications inside lighted rooms, hallways, corridors, lobbies and other areas.

1.4	SUBMITTALS

- Submit under applicable provisions of Section 01 30 00 - ADMINISTRATIVE REQUIREMENTS.

- Data Sheets. Supply the Manufacturer’s technical data sheets for each photoluminescent exit sign type to be furnished.  This information will include the Manufacturer’s UL924 listing documentation and proof that the aluminum construction contains at least 60% post consumer recycled aluminum.

- Manufacturer’s Instructions. Submit Manufacturer’s installation, operation and maintenance instructions for each PL exit sign type to be furnished.

- Installation Drawings, Schedule and Details. Submit Installation Drawings and Schedules for each PL exit sign type indicating where in the building the PL exit signs will be placed and typical elevation and installation details for PL sign placement at doors, walls and other locations.

- Samples.  Submit a full size sample of each photoluminescent exit sign type, style and color to be furnished. Include samples of attachment methods.  If accepted, samples may be installed in project.

1.3 	QUALITY ASSURANCE

A.	Designs, products and installation shall be covered by Section 01 40 00 - QUALITY REQUIREMENTS.

  - All signs, frames, instructions and installation materials supplied shall comply with the applicable requirements of:

1.   UL 924:  Underwriters Laboratories Standard for Emergency Lighting and Power Equipment, Latest Edition.

- State and Local Building and Fire Codes.

- NFPA 101:  National Fire Protection Association Life Safety Code, Latest Edition

- The local Authority Having Jurisdiction (AHJ).

PART 2  PRODUCTS

2.1	SUPPLIERS

- Acceptable Manufacturer.  Series 8924 supplied by ADDLight, 559 Griffith Rd., Charlotte, NC   28217.  Toll Free:  888-367-1010, Tel:  704-525-6210, Fax:  704-525-6310.

- Substitutions:  Not permitted.

- Requests for substitutions will be considered in accordance with provisions of Section 01600 – PRODUCT SUBSTITUTION PROCEDURES.  Acceptable substitutions must be aluminum photoluminescent exit sign faces, frames and mounting brackets constructed of at least 60% post consumer recycled aluminum, have a minimum 75 ft viewing distance and conform to the requirements of UL924 clearly marked on the sign.  Or, where lighting is not sufficient to properly charge photoluminescent exit signs, energy efficient LED exit signs constructed of sustainable materials- aluminum, steel or plastic containing no PVC or vinyl- are permitted.  Radioluminescent exit signs (containing radioactive tritium gas) are not allowed.

2.2	ABOVE THE DOOR (HIGH LEVEL) PHOTOLUMINESCENT EXIT SIGNS

- Exit signs & frames mounted directly to the wall or door.

- Sign & Frame Dimensions.  Supply assembled signs and frames with the following approximate dimensions:  9.0” high x 14.25” wide x 0.75” deep.

- Sign Faceplate Material and Finish.  Supply signs with a [specify red, green or black] ceramic (wear resistant) coated face.  The frame shall be [specify anodized aluminum or black].  The sign and frame shall have a non-glare surface.

- Sign Letters and Directional Arrows. Supply signs with photoluminescent green luminous letters and directional arrows.  Directional arrows shall be non-vinyl or PVC chevron decals.

- Sign Orientation. All wall and door mounted signs are single face exit signs and shall be located in accordance with the Installation Schedule.  Chevron decals can be installed after the sign is installed and the directional marking is certain.

- Sign Attachment. For wall or door mounted signs (without a mounting bracket), supply stainless steel screws (completely non-reactive with all building materials).  Single side signs and frames can be installed above (or beside) the door frame or near floor level on or beside the door.

- Exit signs & frames installed on the wall or ceiling using a mounting bracket.

- Sign & Frame Dimensions.  Supply assembled signs and frames with the following approximate dimensions:  9.0” high x 14.25” wide x 0.75” deep.  Mounting bracket dimensions are 5.0” wide x 2.0” wide x 1.5” deep and it provides a 1.25 inch stand off from the wall or ceiling and can be used on either side or top of the frame.

- Sign Faceplate Material and Finish.  Supply signs with a [specify red, green or black] ceramic (wear resistant) coated face.  The frame shall be [specify anodized aluminum or black].  The sign and frame shall have a non-glare surface.

- Sign Letters and Directional Arrows. Supply signs with photoluminescent green luminous letters and directional arrows.  Directional arrows shall be non-vinyl or PVC chevron decals.

- Sign Orientation. Supply single face or double face signs and mounting brackets in accordance with the Installation Schedule.  Chevron decals can be installed after the sign is installed and the directional marking is certain.

- Sign Attachment. For wall or door mounted signs with a mounting bracket, supply stainless steel screws (completely non-reactive with all building materials).  Single and double side signs, frames and mounting brackets can be installed above (or beside) the door frame.

2.3	FLOOR LEVEL (LOW LEVEL) PHOTOLUMINESCENT EXIT SIGNS

- Exit signs installed without the frame and mounted directly to the wall or door.

- Sign & Frame Dimensions.  Supply assembled signs and frames with the following approximate dimensions:  9.0” high x 14.25” wide x 0.75” deep.

- Sign Faceplate Material and Finish.  Supply signs with a [specify red, green or black] ceramic (wear resistant) coated face.  The frame shall be [specify anodized aluminum or black].  The sign and frame shall have a non-glare surface.

- Sign Letters and Directional Arrows. Supply signs with photoluminescent green luminous letters and directional arrows.  Directional arrows shall be non-vinyl or PVC chevron decals.

- Sign Orientation. All wall and door mounted signs are single face exit signs and shall be located in accordance with the Installation Schedule.  Chevron decals can be installed after the sign is installed and the directional marking is certain.

- Sign Attachment. For wall or door mounted signs (without a mounting bracket), supply stainless steel screws (completely non-reactive with all building materials).  Single side signs and frames can be installed above (or beside) the door frame or near floor level on or beside the door.

- Exit signs & frames mounted directly to the wall or door.

- Sign & Frame Dimensions.  Supply assembled signs and frames with the following approximate dimensions:  9.0” high x 14.25” wide x 0.75” deep.

- Sign Faceplate Material and Finish.  Supply signs with a [specify red, green or black] ceramic (wear resistant) coated face.  The frame shall be [specify anodized aluminum or black].  The sign and frame shall have a non-glare surface.

- Sign Letters and Directional Arrows. Supply signs with photoluminescent green luminous letters and directional arrows.  Directional arrows shall be non-vinyl or PVC chevron decals.

- Sign Orientation. All wall and door mounted signs are single face exit signs and shall be located in accordance with the Installation Schedule.  Chevron decals can be installed after the sign is installed and the directional marking is certain.

- Sign Attachment. For wall or door mounted signs (without a mounting bracket), supply stainless steel screws (completely non-reactive with all building materials).  Single side signs and frames can be installed above (or beside) the door frame or near floor level on or beside the door.

PART 3 EXECUTION

3.1 	ENGINEERING

- The lighting plan will be designed to support the use of photoluminescent exit signs except in those locations where installing proper fluorescent illumination results in significant economic consequences that do not adversely affect the reliability and effectiveness of exit signs and other life safety systems.

- The lighting plan will provide at least 5 foot-candles (54 lux) of illumination on the face of each PL exit sign.  Fluorescent lighting is consistent with the manufacturer’s requirements as indicated on the face of the exit sign.

- The fluorescent lighting fixture(s) designated to provide this illumination is to be operational when the area served by the PL exit sign is occupied.

- The lighting fixture designated to provide illumination for each exit sign will not be switched by occupancy sensors or timers that can turn the lighting fixtures off while the area is occupied.  The lighting fixture providing illumination for each exit signs will not be controlled by dimming controllers that will decrease illumination below 5 foot-candles (54 lux) on the face of the sign while the area served by the PL exit sign is occupied.

3.2	INSTALLATION

- Delivery, Storage and Handling.  Deliver exit signs, frames and mounting hardware to work site and protect from damage until installation.

- Pre-installation Conference: Notify Architect when signs are ready for installation.  Arrange for conference at site.  Do not proceed with installation until receiving Architect’s approval for specific sign locations and method of attachment has been obtained.

- Install signs in accordance with this Specification, local building codes, manufacturer's instructions and as shown on the drawings and as specified by Architect.  Report all conflicts to the Architect.

- Align, level and mount signs uniformly after painting and finishing have been completed and specific wall, ceiling or door surfaces are acceptable to installer.

- Avoid interference with and provide clearance for other equipment. Where the indicated locations for the signs conflicts with locations for other equipment, change the locations of the signs by the minimum distances necessary as approved by the Architect.  Maximum spacing between exit signs shall not exceed 150 feet.

- Install directional chevrons as shown on installation drawings and details.  Take care to properly install chevrons as necessary for each sign.  Once installed, chevron decals cannot be repositioned.

- Repair or replace damaged signs as directed by Architect.

- For signs mounted directly to walls, install with mechanical fasteners (screws and wall anchors are provided).  Low VOC silicone or polyurethane adhesive or double face tape can be used with the mechanical fasteners for additional security.  Double face tape or adhesive by itself is not permitted and is insufficient for a permanent installation.  Eliminate gaps between the wall and the frame or sign.  Follow manufacturer’s instructions for proper installation of signs and frames.

- At completion of installation, clean soiled surfaces following adhesive manufacturer’s instructions.

- Protect installed signs from damage from other construction activities until Acceptance.

3.3  FIELD QUALITY CONTROL

- Turn on the light fixtures that will illuminate the photoluminescent exit signs.

- With an appropriate light meter, measure the amount of illumination on the face of each PL exit sign.

- Report any locations that do not have at least 5 foot-candles (53.8 lux) of illumination by fluorescent lighting fixtures on the face of the exit sign to the project architect.

END OF SECTION